## Sheet1
THIS TOOL IS FOR CX35 AND CX50-2 ONLY
FOR OTHER CHILTRIX VERSIONS SEE
| https://www.chiltrix.com/dynamic-heat-reset/ |  |  | Temps in °C
| Offset | Max Temp | Start targ temp | Start Au Outdoor temp | Ramp Curve | Offset: adjust the curve left or right
Enter Value | -5 | 40 | 25 | 18 | 4 | Max Temp: max temp of AC target (entering water temp)
Range: | -10 to 10 | 35-50 | 20-45 | -10 to 20 | 1 to 5 | Start Targ Temp: the starting temp of the water when au is activated, could also be looked at as min temp of au.
P Value | P49 | P48 | P25 | P24 | P26 | Start Au Outdoor temp: Au is only active when ambient temp is below this temperature.
Ramp Curve: This changes the slope of the curve. Higer number is more gradual.
Outputs
[7 empty] | Outdoor sample temp | Target temp w/o max and min | trg temp max and min
[7 empty] | 35 | 17.5 | #N/A
[7 empty] | 30 | 12.5 | #N/A
[7 empty] | 25 | 16.25 | #N/A
[7 empty] | 20 | 20 | #N/A
[7 empty] | 15 | 23.75 | 25
[7 empty] | 10 | 27.5 | 27.5
[7 empty] | 5 | 31.25 | 31.25
[7 empty] | 0 | 35 | 35
[7 empty] | -5 | 38.75 | 38.75
| You can use this tool to play with different settings to define the curve according to your application. | [5 empty] | -10 | 42.5 | 40
| Once you have a desired curve, set the desired parameters (P Values) into the CX34 controller. | [5 empty] | -15 | 46.25 | 40
| IMPORTANT NOTE: THE TEMP (C) VALUES SHOWN IN THE CHART AND ENTERED ARE RETURN WATER TEMP VALUES. LEAVING (SUPPLY) WATER TEMP WILL BE ~5C HIGHER | [5 empty] | -20 | 50 | 40
35
35
35