## Sheet1
|  | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -3 | -2 | -1 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 22 | 22 | 22
|  | -15 | -14 | -13 | -12 | -11 | -10 | -9 | -8 | -7 | -6 | -5 | -4 | -3 | -2 | -1 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
THIS TOOL IS FOR CX34-4 AND CX50-1 ONLY |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 48.75 | 47.5 | 46.25 | 45 | 43.75 | 42.5 | 41.25 | 40 | 38.75 | 37.5 | 36.25 | 35 | 33.75 | 32.5
FOR OTHER CHILTRIX VERSIONS SEE
https://www.chiltrix.com/dynamic-heat-reset/
P45 offset temp Allowed range -15to15C | 10
P46 Max temp Allowed range 30 to 50C | 50
Requires software version
HMI Version ending in 725 or higher
Main Board Version ending in V53-25 or higher
Temps in C°
You can use this tool to play with different P45/P46 settings to define the curve according to your application.
Once you have a desired curve, set the desired P45/P46 parameters into the CX34 controller.
IMPORTANT NOTE: THE TEMP (C) VALUES SHOWN IN THE CHART AND ENTERED in P48/P49 ARE RETURN WATER TEMP VALUES. LEAVING (SUPPLY) WATER TEMP WILL BE ~5C HIGHER
Heating temperature(℃)
Outdoor temperature （℃）