## Sheet1
THIS TOOL IS FOR CX35 AND CX50-2 ONLY
FOR OTHER CHILTRIX VERSIONS SEE
| https://www.chiltrix.com/dynamic-heat-reset/ |  |  | Temps in °C
INPUTS
| P49: Offset | P48: Max Temp | P25: Start targ temp | P24: Start Au Outdoor temp | P26: Ramp Curve | Offset: adjust the curve left or right
| -10 | 35 | 24 | 20 | 5 | Max Temp: max temp of entering water
Range: | -10 to 10 | 35-50 | 20-45 | -10 to 20 | 1 to 5 | Start Targ Temp: the starting temp of the water when au is activated, could also be looked at as min temp of au.
Start Au Outdoor temp: Au is only active when ambient temp is below this temperature.
Ramp Curve: This changes the slope of the curve. Higer number is more gradual.
Make sure to enable Heating Au in the mode menu of the main controler, shown on the mode section of the manual.
Outputs
[7 empty] | Outdoor sample temp | Target temp w/o max and min | trg temp max and min
[7 empty] | 35 | 16 | #N/A
[7 empty] | 30 | 12 | #N/A
[7 empty] | 25 | 15 | #N/A
[7 empty] | 20 | 18 | 24
[7 empty] | 15 | 21 | 24
[7 empty] | 10 | 24 | 24
[7 empty] | 5 | 27 | 27
[7 empty] | 0 | 30 | 30
[7 empty] | -5 | 33 | 33
| You can use this tool to play with different settings to define the curve according to your application. | [5 empty] | -10 | 36 | 35
| Once you have a desired curve, set the desired parameters (P Values) into the CX35/50 controller. | [5 empty] | -15 | 39 | 35
| IMPORTANT NOTE: THE TEMP (C) VALUES SHOWN IN THE CHART AND ENTERED ARE RETURN WATER TEMP VALUES. LEAVING (SUPPLY) WATER TEMP WILL BE ~5C HIGHER | [5 empty] | -20 | 42 | 35
[7 empty] | -25 | 45 | 35
[7 empty] | -30 | 48 | 35
30